EXPERIMENT:	Refrigeration Gas Charging Unit

OBJECTIVES:

- To identify the component of gas charging unit

COMPONENTS OF GAS CHARGING UNIT:

- Rotary vacuum pump		- This is used for vacuum the system to be charged.

- Charging cylinder		- This is used to fill the refrigerant from the refrigerant bottle.

- Manifold & Gauges		- Four way manifold with sight glass and glycerin filled gauges.

Compound gauge 	- blue

Pressure gauge	- red

- Vacuum gauge		- Directly connected on to 4 way manifold with separate valve and incorporated safety valve for protection of vacuum against over pressure.

PROCEDURE:

- Charging of Cylinder with Refrigerant

- Close all valves.

- Connect refrigerant bottle by means of charging line with valve F of charging cylinder.

- Put vacuum pump in to operation.

- Open valves A, D, E, F.

- Evacuate for 2 – 5 minutes.

- Close valve D and check with vacuum gauge if vacuum remains in the system.

- Switch off the vacuum pump.

- Close valves A and E.

- Open slowly the valve at the refrigerant bottle. The refrigerant enters in to the charging cylinder level can be controlled at the sight glass.

- As soon as pressure of charging cylinder and refrigerant bottle is equal, handle the valve G.

- The charging cylinder has to be charged only scale boarder. Don’t over charge.

- Close valve E and remove refrigerant bottle.

- Evacuating a Refrigerant System

- Connect refrigeration system with compound gauge (valve B) and pressure gauge (valve C).

- Switch on the vacuum pump.

- Open slowly valves B & D. If C is connected with system open as well.

- If compound gauge does not show over pressure, open valve A.

- Switch on the compressor of the refrigeration system for approximately 3 minutes.

- Close valve A.

- By closing valve D and shortly opening valve E (Approximately 5 seconds for freezers and 10 seconds for deep freezers) the system can be flushed.

- Close valve E and open again valve D.

- Evacuate once again for 15 to 20 minutes.

- Check the vacuum by closing valve D.

- Charging a Refrigeration System

- System is already evacuated. Valves A, D & E are closed.

- Turn the printed cylinder to see the gas.

- Refrigerant pressure in the charging cylinder is controlled by the gauge mounted on the top of the charging cylinder.

- Now check if pressure of the charging cylinder gauge corresponds with the scale on the sight glass.

Eg. Refrigerant R – 12, pressure indication shows 4.9 bar; by turning around the scale (R-12), the corresponding pressure scale on the sight glass.

- The quantity of refrigerant can be indicated by adjustable plastic circle around the cylinder.

- Open slowly valve E and fill with refrigerant approximately 50 – 70 grams.

- Check the whole system for leaks with electronic leak detector.

- Let the compressor of the refrigerant system run.

- Fill the rest of refrigerant in by opening valve E.

- Disconnect charging station and refrigerant system.